{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["质量流量计"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"质量流量计","index":0,"n_rows":15,"n_cols":39,"rows_kept":15,"flags":["formulas_cached_only"]}
["备注","类别","序号","工段/部门","位号","新位号","仪表名称","测点","介质","设计温度/℃","进口压力/Mpa","操作粘度/cp","操作密度/kg/m3","管径","建议量程","最大允许压降/KPa","最小/正常/最大流量",null,null,"单位","是否配置过滤器","信号输出","现场显示","供电要求","接线制","电气接口","流量精度要求/%","密度精度要求/kg/m3","是否带二次表","是否带温压补偿","接液材质","过程连接形式","法兰尺寸","防爆/防护等级","是否夹套伴热","数量/个/台","申购日期","生产厂家","备注"]
[null,"A",1,41,"FIX101",null,"质量流量计","PR11-4100610流量","油脂",30,0.25,4,880,100,"/",80,10,77,100,"t/h","否","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",0.2,2,"/","否",304,"法兰连接",null,"EXdⅡBT4/IP65","否",1]
[null,"A",2,41,"FIX102",null,"质量流量计","PR11-4100611流量","油脂",30,0.25,4,880,100,"/",80,10,77,100,"t/h","否","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",0.2,2,"/","否",304,"法兰连接",null,"EXdⅡBT4/IP65","否",1]
[null,"A",3,41,"FIX103",null,"质量流量计","PL-4100704流量","油脂",30,0.25,4,880,100,"/",80,10,77,100,"t/h","否","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",0.2,2,"/","否",304,"法兰连接",null,"EXdⅡBT4/IP65","否",1]
[null,"A",4,41,"FIX104",null,"质量流量计","PR30-4101105流量","油脂",30,0.25,100,880,100,"/",100,10,77,100,"t/h","否","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",0.2,2,"/","否","316L","法兰连接",null,"EXdⅡBT4/IP65","否",1]
[null,"A",5,"11a","FICA3104B",null,"质量流量计","P3104醇碱泵出口流量去V3107","甲醇碱溶液",40,0.2,20,800,20,"/",50,0.2,0.7,1,"t/h","否","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",0.3,2,"/","否",304,"法兰连接",null,"EXdⅡBT4/IP65","否",1]
[null,"A",6,"11a","FICA3104A",null,"质量流量计","P3104醇碱泵出口流量去V3105","甲醇碱溶液",40,0.2,20,800,20,"/",50,0.2,0.7,1,"t/h","否","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",0.3,2,"/","否",304,"法兰连接",null,"EXdⅡBT4/IP65","否",1]
[null,"A",7,"11c","FI5308",null,"质量流量计","P5308产品出料泵出口出料流量","油脂",100,0.3,4,860,50,"/",20,3,8,10,"t/h","否","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",0.3,2,"/","否",304,"法兰连接",null,"EXdⅡBT4/IP65","否",1]
[null,"A",8,"11c","FI5408",null,"质量流量计","C18出料泵P5403出料流量","油脂",100,0.3,4,860,50,"/",20,3,8,10,"t/h","否","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",0.3,2,"/","否",304,"法兰连接",null,"EXdⅡBT4/IP65","否",1]
[null,"A",9,"11c","FIA8504",null,"质量流量计","复蒸塔P8503出料流量（1075）","油脂",100,0.3,4,860,50,"/",20,3,8,10,"t/h","否","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",0.3,2,"/","否",304,"法兰连接",null,"EXdⅡBT4/IP65","否",1]
[null,"A",10,"11c","FIA8602","FICA8602","质量流量计","沥青塔P8603出料（1507）流量","油脂",100,0.3,4,860,50,"/",20,0.5,1.2,4,"t/h","否","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",0.3,2,"/","否",304,"法兰连接",null,"EXdⅡBT4/IP65","否",1]
[null,"A",11,"11c","FICA5303",null,"质量流量计","C16塔P5304出料泵1690出料流量","油脂",100,0.3,4,860,32,"/",20,0.3,1,3,"t/h","否","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",0.3,2,"/","否",304,"法兰连接",null,"EXdⅡBT4/IP65","否",1]
[null,"A",12,"11c","FICA8601","FIA8601","质量流量计","沥青塔釜液P8601出料流量（黑脚）","油脂",150,0.3,50,880,50,"/",20,1,5,7,"t/h","否","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",0.3,2,"/","否",304,"法兰连接",null,"EXdⅡBT4/IP65","否",1]
[null,"A",13,"11a","FICA4104",null,"质量流量计","P4108分1020出口流量","甘油",100,0.3,900,1000,50,"/",30,1,2,5,"t/h","否","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",1.5,0.5,"/","否",304,"法兰连接",null,"EXdⅡBT4/IP65","否",1]
[null,"A",14,"11a","FICA1101",null,"质量流量计","P423出口预处理原料流量","油脂",70,0.3,80,890,80,"/",20,7,20,25,"t/h","袋式过滤机（3目）","2路4-20mA+HART","背光LCD","DC24V","2+4线制","M20*1.5",0.3,2,"/","否","316L","法兰连接",null,"EXdⅡBT4/IP65","否",1]