{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["调节阀","分散统计数量"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"调节阀","index":0,"n_rows":120,"n_cols":49,"rows_kept":120,"merged":[[0,0,1,0],[0,1,1,1],[0,2,1,2],[0,3,1,3],[0,4,1,4],[0,5,1,5],[0,6,1,6],[0,7,1,7],[0,8,0,20],[0,21,0,31],[0,32,1,34],[0,35,0,36],[0,37,0,43],[0,45,1,45],[0,46,1,46],[0,47,1,47],[0,48,1,48],[1,12,1,14]],"flags":["formulas_cached_only"]}
["备注","类别","序号","工段/部门","位号","新位号","仪表名称","测点","操作条件",{"$nulls":12},"阀体",{"$nulls":10},"最小/正常/最大流量开度",null,null,"执行机构",null,"定位器",{"$nulls":6},"附件","数量","申购日期","生产厂家","备注"]
[{"$nulls":8},"介质","设计温度","操作密度kg/m3","操作粘度/cp","最小/正常/最大流量",null,null,"单位","进口压力MPa","出口设备压力MPa","最大关闭压差MPa","管道尺寸DN","管道材质","阀体型式","流量特性","泄漏等级","上阀盖形式","阀体材质","阀芯材质","阀杆材质","阀座材质","填料材质","口径","法兰标准及压力等级（RF）",{"$nulls":3},"故障阀位","手轮机构","种类","阀位反馈信号","气源压力MPa","防爆/防护等级","电气接口","接线制","输入信号","减压过滤器（带压力表，排污，气源管接头1/4NPT）"]
[null,"A",1,"11a","PV9403",null,"自力式压力调节阀","1号线蒸汽调节","蒸汽",190,3,"/",1,7,10,"t/h","0.8~1.0","阀后在0.4~0.7MPa之间可调",0.8,200,"碳钢","/","/","Ⅴ","标准型","WCB","304+STL",304,304,"柔性石墨",null,"HG20592-09,PN16",{"$nulls":3},"/","/","/","/","/","/","/","/","/","/",1]
[null,"A",2,"11a","PV9404",null,"自力式压力调节阀","2号线蒸汽调节","蒸汽",190,3,"/",1,7,10,"t/h","0.8~1.0","阀后在0.4~0.7MPa之间可调",0.8,200,"碳钢","/","/","Ⅴ","标准型","WCB","304+STL",304,304,"柔性石墨",null,"HG20592-09,PN16",{"$nulls":3},"/","/","/","/","/","/","/","/","/","/",1]
[null,"B",3,"11a","PV9405",null,"自力式压力调节阀","罐区蒸汽","蒸汽",190,3,"/",0.4,3,4,"t/h","0.8~1.0","阀后在0.4~0.7MPa之间可调",0.8,80,"碳钢","/","/","Ⅴ","标准型","WCB","304+STL",304,304,"柔性石墨","DN80","HG20592-09,PN16",{"$nulls":3},"/","/","/","/","/","/","/","/","/","/",1]
[null,"B",4,"11a","PV9406",null,"自力式压力调节阀","去12车间蒸汽流量","蒸汽",190,3,"/",0.4,2,4,"t/h","0.8~1.0","阀后在0.7~0.9MPa之间可调",0.8,80,"碳钢","/","/","Ⅴ","标准型","WCB","304+STL",304,304,"柔性石墨","DN80","HG20592-09,PN16",{"$nulls":3},"/","/","/","/","/","/","/","/","/","/",1]
[null,"B",5,"11a","TV2111B",null,"气动调节阀","E2106进水量调节","水","常温",1000,1,"/","/","依管径","m3/h",0.2,0,0.2,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",6,"11a","TV2111A",null,"气动调节阀","E2104进水量调节","水","常温",1000,1,"/","/","依管径","m3/h",0.2,0,0.2,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",7,"11a","TV7102","PV7102","气动调节阀","T-7101加热蒸汽压力调节","蒸汽",170,3,"/",0.05,0.1,0.3,"t/h",0.4,0,0.4,25,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",8,"11a","FV3104B",null,"气动调节阀","P3104出口流量去v3108调节","甲醇、KOH",40,800,20,0.1,0.7,1,"m3/h",0.2,0,0.2,20,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN20","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",9,"11a","FV3101B",null,"气动调节阀","P3101出口流量调节","油脂，甲醇，酸",70,870,4,3,15,20,"m3/h",0.2,0,0.2,50,304,"单座","等百分比","Ⅳ","标准型","CF8+PFA","304+PFA","304+PFA","304+PFA","PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",10,"11a","FV3104A",null,"气动调节阀","P3104出口流量调节","甲醇、KOH",40,800,20,0.1,0.7,1,"m3/h",0.2,0,0.2,20,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN20","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",11,"11a","FV3101A",null,"气动调节阀","P3101出口流量调节","油脂，甲醇，酸",70,870,4,3,15,20,"m3/h",0.2,0,0.2,50,304,"单座","等百分比","Ⅳ","标准型","CF8+PFA","304+PFA","304+PFA","304+PFA","PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",12,"11a","FV4103A","LV4103A","气动调节阀","脱醇出料","油脂",110,850,5,3,15,20,"m3/h",0.2,0,0.2,50,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",13,"11a","FV4103B","LV4103B","气动调节阀","脱醇出料","油脂",110,850,5,3,15,20,"m3/h",0.2,0,0.2,50,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",14,"11a","PV1103",null,"气动调节阀","E-1101/1102原料预热蒸汽加热管线调节阀","蒸汽",170,3,"/",0.1,0.3,0.5,"t/h",0.4,0,0.4,32,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",15,"11a","PV2101",null,"气动调节阀","R2101蒸汽加热","蒸汽",170,3,"/",0.1,0.2,0.9,"t/h",0.4,0,0.4,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",16,"11a","PV2102",null,"气动调节阀","R2102蒸汽加热","蒸汽",170,3,"/",0.05,0.1,0.4,"t/h",0.4,0,0.4,32,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",17,"11a","PV2103",null,"气动调节阀","R2103蒸汽加热","蒸汽",170,3,"/",0.1,0.2,0.9,"t/h",0.4,0,0.4,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",18,"11a","PV2108",null,"气动调节阀","E2101甲醇蒸汽加热","蒸汽",170,3,"/",0.3,1.2,1.6,"t/h",0.4,0,0.4,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",19,"11a","PV2201",null,"气动调节阀","R2201蒸汽加热","蒸汽",170,3,"/",0.1,0.2,0.9,"t/h",0.4,0,0.4,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",20,"11a","PV2202",null,"气动调节阀","R2202蒸汽加热","蒸汽",170,3,"/",0.05,0.1,0.4,"t/h",0.4,0,0.4,32,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",21,"11a","PV2203",null,"气动调节阀","R2203蒸汽加热","蒸汽",170,3,"/",0.1,0.2,0.9,"t/h",0.4,0,0.4,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",22,"11a","PV2208",null,"气动调节阀","E2201蒸汽加热","蒸汽",170,3,"/",0.3,1.2,1.6,"t/h",0.4,0,0.4,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",23,"11a","PV6106",null,"气动调节阀","甲醇塔釜蒸汽加热","蒸汽",170,3,"/",0.05,0.3,0.4,"t/h",0.4,0,0.4,32,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",24,"11a","PV6206",null,"气动调节阀","甲醇塔釜蒸汽加热","蒸汽",170,3,"/",0.05,0.3,0.4,"t/h",0.4,0,0.4,32,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",25,"11a","LV2104",null,"气动调节阀","1号釜出料","油脂，甲醇，酸",120,840,5,3,15,20,"m3/h",0.2,0.01,0.2,50,"衬氟","单座","等百分比","Ⅳ","标准型","CF8+PFA","304+PFA","304+PFA","304+PFA","PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",26,"11a","LV2105",null,"气动调节阀","2号釜出料","油脂，甲醇，酸",120,840,5,3,15,20,"m3/h",0.2,0.16,0.2,50,"衬氟","单座","等百分比","Ⅳ","标准型","CF8+PFA","304+PFA","304+PFA","304+PFA","PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",27,"11a","LV2106",null,"气动调节阀","3号釜出料","油脂，甲醇，酸",120,840,5,3,15,20,"m3/h",0.2,-0.06,0.2,50,"衬氟","单座","等百分比","Ⅳ","标准型","CF8+PFA","304+PFA","304+PFA","304+PFA","PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",28,"11a","LV2107",null,"气动调节阀","4号釜出料","油脂，甲醇，酸",80,840,5,3,15,20,"m3/h",0.2,0,0.2,50,"衬氟","单座","等百分比","Ⅳ","标准型","CF8+PFA","304+PFA","304+PFA","304+PFA","PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",29,"11a","LV2202",null,"气动调节阀","1号釜出料","油脂，甲醇，酸",120,840,5,3,15,20,"m3/h",0.2,0.01,0.2,50,"衬氟","单座","等百分比","Ⅳ","标准型","CF8+PFA","304+PFA","304+PFA","304+PFA","PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",30,"11a","LV2203",null,"气动调节阀","2号釜出料","油脂，甲醇，酸",120,840,5,3,15,20,"m3/h",0.2,0.16,0.2,50,"衬氟","单座","等百分比","Ⅳ","标准型","CF8+PFA","304+PFA","304+PFA","304+PFA","PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",31,"11a","LV2204",null,"气动调节阀","3号釜出料","油脂，甲醇，酸",120,840,5,3,15,20,"m3/h",0.2,-0.06,0.2,50,"衬氟","单座","等百分比","Ⅳ","标准型","CF8+PFA","304+PFA","304+PFA","304+PFA","PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",32,"11a","LV2205",null,"气动调节阀","4号釜出料","油脂，甲醇，酸",80,840,5,3,15,20,"m3/h",0.2,0,0.2,50,"衬氟","单座","等百分比","Ⅳ","标准型","CF8+PFA","304+PFA","304+PFA","304+PFA","PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",33,"11a","TV1110",null,"气动调节阀","热水罐蒸汽加热","蒸汽",170,3,"/",0.05,0.1,0.3,"t/h",0.4,0,0.4,25,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",34,"11a","TV3103",null,"气动调节阀","E3103加热蒸汽调节阀","蒸汽",170,3,"/",0.05,0.1,0.3,"t/h",0.4,0,0.4,25,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",35,"11a","TV3104",null,"气动调节阀","E3102加热蒸汽调节阀","蒸汽",170,3,"/",0.05,0.1,0.3,"t/h",0.4,0,0.4,25,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",36,"11a","TV4102",null,"气动调节阀","E4101加热蒸汽调节阀","蒸汽",170,3,"/",0.2,1.1,1.4,"t/h",0.4,0,0.4,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",37,"11a","TV4103",null,"气动调节阀","T4101加热","蒸汽",170,3,"/",0.5,0.8,1,"t/h",0.4,0,0.4,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",38,"11a","TV4104",null,"气动调节阀","E4101加热低压气调节阀","蒸汽",170,3,"/",0.5,0.8,1,"t/h",0.2,0,0.2,80,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN80","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",39,"11a","TV6102",null,"气动调节阀","R6101高压气调节","蒸汽",170,3,"/",0.1,0.8,1,"t/h",0.4,0,0.4,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",40,"11a","TV6101",null,"气动调节阀","T6101甲醇回流流量调节","甲醇",35,791,0.6,1.5,5,7,"m3/h",0.2,0,0.2,32,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",41,"11a","TV6103",null,"气动调节阀","R6101低压气调节","蒸汽",170,3,"/",0.2,0.8,1,"t/h",0.2,0,0.2,80,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN80","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",42,"11a","TV6202",null,"气动调节阀","R6201高压气调节","蒸汽",170,3,"/",0.1,0.8,1,"t/h",0.4,0,0.4,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",43,"11a","TV6201",null,"气动调节阀","T6201甲醇回流流量调节","甲醇",35,791,0.6,1.5,5,7,"m3/h",0.2,0,0.2,32,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",44,"11a","TV6203",null,"气动调节阀","R6201低压气调节","蒸汽",170,3,"/",0.2,0.8,1,"t/h",0.2,0,0.2,80,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN80","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",45,"11a","LV2108",null,"气动调节阀","酯化甲醇出料","甲醇",50,791,0.6,1,3,5,"m3/h",0.2,0,0.2,25,"碳钢","单座","等百分比","Ⅳ","标准型","CF8","316L","316L","316L","PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",46,"11a","LV2206",null,"气动调节阀","酯化甲醇出料","甲醇",35,791,0.6,1,3,5,"m3/h",0.2,0,0.2,25,"碳钢","单座","等百分比","Ⅳ","标准型","CF8","316L","316L","316L","PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",47,"11a","LV3105",null,"气动调节阀","酯交换出料","油脂，KOH",64,820,2,3,10,15,"m3/h",0.2,0.005,0.2,65,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,"316L","PTFE","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",48,"11a","LV3106",null,"气动调节阀","酯交换出料","油脂，KOH",60,820,2,3,10,15,"m3/h",0.2,0.005,0.2,65,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",49,"11a","LV4104",null,"气动调节阀","脱醇甲醇","甲醇",35,791,0.6,3,6,8,"m3/h",0.2,0,0.2,32,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",50,"11a","LV6104",null,"气动调节阀","甲醇废水","水，甲醇",100,1000,0.3,0.4,0.8,2,"m3/h",0.3,0,0.3,25,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",51,"11a","LV6102",null,"气动调节阀","出料流量","甲醇",35,791,0.6,1,2.5,5,"m3/h",0.2,0,0.2,25,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",52,"11a","LV6103",null,"气动调节阀","出料流量","甲醇",35,791,0.6,1,2.5,5,"m3/h",0.2,0,0.2,25,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",53,"11a","LV6204",null,"气动调节阀","甲醇废水","水，甲醇",100,1000,0.3,0.4,0.8,2,"m3/h",0.3,0,0.3,25,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",54,"11a","LV6202",null,"气动调节阀","出料流量","甲醇",40,791,0.6,1,2.5,5,"m3/h",0.2,0,0.2,25,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",55,"11a","LV6203",null,"气动调节阀","出料流量","甲醇",40,791,0.6,1,2.5,5,"m3/h",0.2,0,0.2,25,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",56,"11a","FV1101",null,"气动调节阀","预处理原料","油脂",50,890,80,5,25,35,"t/h",0.3,0.005,0.3,80,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN80","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",57,"11a","FV1102",null,"气动调节阀","热水","水",95,1000,0.3,0.5,2,5,"m3/h",0.2,0.005,0.2,25,"碳钢","单座","等百分比","Ⅳ","标准型","WCB",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",58,"11a","FV1103","HV1103","气动调节阀","水洗沉降","水，油脂，机械杂质",90,980,1,0.5,2,4,"m3/h",0.15,0,0.15,32,304,"V型球阀","等百分比","Ⅳ","标准型","CF8","316L+STL","316L","316L","PTFE","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",59,"11a","FV2101",null,"气动调节阀","酯化原料","油脂",80,880,30,3,15,20,"m3/h",0.3,0,0.3,50,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",60,"11a","FV2103",null,"气动调节阀","酯化甲醇","甲醇","常温",791,0.6,1,4,6,"m3/h",0.4,0.25,0.4,25,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",61,"11a","FV2201",null,"气动调节阀","酯化原料","油脂",100,880,8,3,15,20,"m3/h",0.3,0,0.3,50,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",62,"11a","FV2203",null,"气动调节阀","酯化甲醇","甲醇","常温",791,0.6,1,4,6,"m3/h",0.4,0.25,0.4,25,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",63,"11a","FV3103",null,"气动调节阀","酯交换甲醇","甲醇",35,791,0.6,1,3,5,"m3/h",0.2,0,0.2,25,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",64,"11a","FV3105",null,"气动调节阀","酯交换甲醇","甲醇",35,791,0.6,1,3,5,"m3/h",0.2,0,0.2,25,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",65,"11a","FV3107",null,"气动调节阀","分含醇甘油","甘油、甲醇、油脂",50,1100,20,0.5,1.2,3,"m3/h",0.2,0.01,0.2,25,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",66,"11a","FV3109",null,"气动调节阀","含醇甘油处理前","甘油、甲醇、油脂",50,1100,20,0.5,3,5,"m3/h",0.2,0.01,0.2,32,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",67,"11a","FV4102",null,"气动调节阀","脱醇进料","油脂，甲醇",60,850,5,5,36,42,"m3/h",0.2,0.02,0.2,65,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",68,"11a","FV4105",null,"气动调节阀","去甲酯塔","油脂",100,850,5,4,15,20,"m3/h",0.3,-0.095,0.3,50,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",69,"11a","FV4106",null,"气动调节阀","P4106出口流量调节","油脂",80,850,5,4,15,20,"m3/h",0.3,0.002,0.3,50,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",70,"11a","TV7101",null,"气动调节阀","脱醇加热器7101蒸汽加热","蒸汽",170,3,"/",0.5,0.8,1,"t/h",0.4,0,0.4,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",71,"11a","LV7101",null,"气动调节阀","脱醇出料流量调节","甘油、油脂",110,1300,100,1,3.6,5,"m3/h",0.2,0.01,0.2,32,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",72,"11a","LV7102",null,"气动调节阀","甲醇出料泵流量调节","甲醇",40,791,0.6,0.3,2,3,"m3/h",0.2,0,0.2,25,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",73,"11a","LV7106",null,"气动调节阀","甲醇出料泵流量调节","甲醇",40,791,0.6,0.3,2,3,"m3/h",0.2,0,0.2,25,"碳钢","单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
["取消","B",74,"11c","HV5201",null,"气动调节阀","P5204出口流量调节","油脂",60,870,4,1,3,5,"m3/h",0.3,0,0.3,25,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1,null,null,"取消，换开关阀，是否需要再确认"]
[null,"B",75,"11c","HV8505","FV8505","气动调节阀","P8503回流流量调节","油脂",180,860,4,1,2,6,"m3/h",0.3,-0.097,0.3,25,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"柔性石墨","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",76,"11c","HV8506","LV8506","气动调节阀","P8503出料调节","油脂",100,860,4,3,8,10,"t/h",0.3,0,0.3,50,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",77,"11c","HV8507","LV8507","气动调节阀","P8504A回流流量调节","油脂",180,860,4,2,7,15,"m3/h",0.3,-0.097,0.3,50,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",78,"11c","FV5301","LV5301","气动调节阀","16去18塔调节","油脂",130,860,4,2,14,17,"m3/h",0.2,-0.097,0.2,50,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",79,"11c","FV5302","LV5302","气动调节阀","P5303AB回流流量调节","油脂",180,820,4,2,8,15,"m3/h",0.3,-0.097,0.3,50,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",80,"11c","LV8510",null,"气动调节阀","P8510出料调节","油脂",40,920,2,0.5,0.8,1,"m3/h",0.2,0,0.2,25,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",81,"11c","FV5303",null,"气动调节阀","C16出料调节","油脂",100,860,4,0.25,1,2,"t/h",0.3,0,0.3,32,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",82,"11c","FV5307",null,"气动调节阀","P5308出口回流流量调节","油脂",210,870,4,1,2,6,"m3/h",0.3,-0.097,0.3,25,304,"单座","等百分比","Ⅳ","散热型","CF8","304+STL",304,304,"柔性石墨","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",83,"11c","FV5401","LV5401","气动调节阀","18塔去沥青塔流量调节","油脂",260,860,4,1,3,8,"m3/h",0.2,-0.097,0.2,32,304,"单座","等百分比","Ⅳ","散热型","CF8","304+STL",304,304,"柔性石墨","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",84,"11c","FV5402","LV5402","气动调节阀","P5404AB回流流量调节","油脂",180,860,4,2,8,15,"m3/h",0.3,-0.097,0.3,50,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",85,"11c","FV5403","HV5403","气动调节阀","P5404AB出料调节","油脂",60,870,4,1,4,5,"m3/h",0.3,0,0.3,25,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",86,"11c","FV5407",null,"气动调节阀","P5403回流流量调节","油脂",180,820,4,1,2,6,"m3/h",0.3,-0.097,0.3,25,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"柔性石墨","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",87,"11c","FV8501","LV8501","气动调节阀","P8502出料流量调节","油脂",250,760,4,2,3,12,"m3/h",0.2,0,0.2,50,304,"单座","等百分比","Ⅳ","散热型","CF8","304+STL",304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",88,"11c","FV8601","LV8601","气动调节阀","P8601出料流量调节","油脂",150,880,50,3,6,10,"t/h",0.3,0,0.3,50,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",89,"11c","LV5102",null,"气动调节阀","P5101出料去16塔液位调节","油脂",120,870,4,3,14,17,"m3/h",0.2,-0.097,0.2,50,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",90,"11c","LV5103",null,"气动调节阀","P5101出料去18塔液位调节","油脂",120,870,4,3,14,17,"m3/h",0.2,-0.097,0.2,50,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",91,"11c","LV5201",null,"气动调节阀","P5202出料液位调节","油脂",220,820,4,3,14,17,"m3/h",0.2,-0.097,0.2,50,304,"单座","等百分比","Ⅳ","散热型","CF8","304+STL",304,304,"柔性石墨","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",92,"11c","LV5202",null,"气动调节阀","P5203A回流液位调节","油脂",140,860,4,1,3,10,"m3/h",0.3,-0.097,0.3,40,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"柔性石墨","DN40","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",93,"11c","FV5203",null,"气动调节阀","1067复蒸去脱轻塔进料","油脂",50,870,4,5,12,15,"m3/h",0.2,-0.097,0.2,65,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",94,"11c","LV8602",null,"气动调节阀","P8603出料液位调节","油脂",100,860,4,0.4,1.2,3.5,"t/h",0.3,-0.097,0.3,50,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",95,"11c","TV5101","PV5101","气动调节阀","T-5101蒸汽加热温度调节","蒸汽",170,3,"/",0.05,0.1,0.3,"t/h",0.4,0,0.4,25,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",96,"11c","TV5204",null,"气动调节阀","脱臭塔导热油加热温度调节1","导热油",300,880,6,"/","/","依管径","m3/h",0.3,0,0.3,65,"碳钢","单座","等百分比","Ⅳ","波纹管密封型","WCB","304+STL",304,304,"柔性石墨","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",97,"11c","TV5206",null,"气动调节阀","脱臭塔导热油加热温度调节2","导热油",300,880,6,"/","/","依管径","m3/h",0.3,0,0.3,65,"碳钢","单座","等百分比","Ⅳ","波纹管密封型","WCB","304+STL",304,304,"柔性石墨","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",98,"11c","TV5305",null,"气动调节阀","16塔导热油加热温度调节1","导热油",300,880,6,"/","/","依管径","m3/h",0.3,0,0.3,65,"碳钢","单座","等百分比","Ⅳ","波纹管密封型","WCB","304+STL",304,304,"柔性石墨","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",99,"11c","TV5307",null,"气动调节阀","16塔导热油加热温度调节2","导热油",300,880,6,"/","/","依管径","m3/h",0.3,0,0.3,65,"碳钢","单座","等百分比","Ⅳ","波纹管密封型","WCB","304+STL",304,304,"柔性石墨","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",100,"11c","HV5412","TV5412","气动调节阀","18塔导热油加热温度调节1","导热油",300,880,6,"/","/","依管径","m3/h",0.3,0,0.3,65,"碳钢","单座","等百分比","Ⅳ","波纹管密封型","WCB","304+STL",304,304,"柔性石墨","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",101,"11c","HV5413","TV5413","气动调节阀","18塔导热油加热温度调节2","导热油",300,880,6,"/","/","依管径","m3/h",0.3,0,0.3,65,"碳钢","单座","等百分比","Ⅳ","波纹管密封型","WCB","304+STL",304,304,"柔性石墨","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",102,"11c","HV8512","TV8512","气动调节阀","复蒸塔导热油加热温度调节1","导热油",300,880,6,"/","/","依管径","m3/h",0.3,0,0.3,65,"碳钢","单座","等百分比","Ⅳ","波纹管密封型","WCB","304+STL",304,304,"柔性石墨","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",103,"11c","HV8513","TV8513","气动调节阀","复蒸塔导热油加热温度调节2","导热油",300,880,6,"/","/","依管径","m3/h",0.3,0,0.3,65,"碳钢","单座","等百分比","Ⅳ","波纹管密封型","WCB","304+STL",304,304,"柔性石墨","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",104,"11c","TV8604",null,"气动调节阀","沥青塔导热油加热温度调节1","导热油",300,880,6,"/","/","依管径","m3/h",0.3,0,0.3,65,"碳钢","单座","等百分比","Ⅳ","波纹管密封型","WCB","304+STL",304,304,"柔性石墨","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"A",105,"11c","TV8606",null,"气动调节阀","沥青塔导热油加热温度调节2","导热油",300,880,6,"/","/","依管径","m3/h",0.3,0,0.3,65,"碳钢","单座","等百分比","Ⅳ","波纹管密封型","WCB","304+STL",304,304,"柔性石墨","DN65","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",106,"11c","FV5308","LV5308","气动调节阀","P5308出料流量调节","油脂",100,860,4,3,8,10,"t/h",0.3,0.02,0.3,50,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",107,"11c","FV5408","LV5408","气动调节阀","P5403出料调节","油脂",100,860,4,3,8,10,"t/h",0.3,0.02,0.3,50,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",108,"11c","LV5409",null,"气动调节阀","P5412出料调节","油脂，甲醇",40,920,2,0.5,0.8,1,"m3/h",0.2,0,0.2,25,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
["取消","B",109,"11c","LV5411",null,"气动调节阀","P5411出料去罐区调节","油脂，甲醇",30,920,2,2,4,5,"m3/h",0.3,0,0.3,25,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
["取消","B",110,"11c","LV5412",null,"气动调节阀","P5411出料去甲醇塔调节","油脂，甲醇",30,920,2,2,4,5,"m3/h",0.3,0,0.3,25,304,"单座","等百分比","Ⅳ","标准型","CF8",304,304,304,"PTFE","DN25","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",111,"11a","LV9401",null,"气动调节阀","v9401液位调节","水",95,1000,1,2,10,20,"m3/h",0.3,0,0.3,50,"碳钢","单座","等百分比","Ⅳ","标准型","WCB",304,304,304,"PTFE","DN50","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",112,41,"TV1101",null,"气动调节阀","E1107原料预热器出口温度调节","蒸汽",170,3,"/",0.05,0.1,0.4,"t/h",0.4,0,0.4,32,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",113,41,"TV1102",null,"气动调节阀","E1108原料预热器出口温度调节","蒸汽",170,3,"/",0.05,0.1,0.4,"t/h",0.4,0,0.4,32,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN32","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",114,"11c","PV5201",null,"气动调节阀","V5203蒸汽包出口压力调节","蒸汽",170,3,"/",0.2,0.8,1,"t/h",0.2,0,0.2,100,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN80","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",115,"11c","PV5401",null,"气动调节阀","V5405蒸汽包出口压力调节","蒸汽",170,3,"/",0.2,0.8,1,"t/h",0.2,0,0.2,100,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN80","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[null,"B",116,"11c","PV8501",null,"气动调节阀","V8505蒸汽包出口压力调节","蒸汽",170,3,"/",0.2,0.8,1,"t/h",0.2,0,0.2,100,"碳钢","单座","等百分比","Ⅳ","标准型","WCB","304+STL",304,304,"柔性石墨","DN80","HG20592-09,PN16",{"$nulls":3},"故障关","否","机械型","否","0.4~0.7","EXdⅡBT4/IP65","M20*1.5","2线制","4-20mA","是",1]
[]
[null,"总计113台"]

{"sheet":"分散统计数量","index":1,"n_rows":6,"n_cols":2,"rows_kept":6,"flags":["formulas_cached_only"]}
["名称","数量"]
["自力式压力调节阀",4]
["气动调节阀",109]
[]
[]
["总计",113]