{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":52,"n_cols":7,"rows_kept":52,"flags":["formulas_cached_only"]}
["序号","位号","名称","参数要求","数量","总长度","备注"]
[1,"XV401","气动切断阀","DN125，对夹式蝶阀，-10℃，壳体：球墨铸铁，内件：304,内衬PTFE 介质：油脂，隔爆，带机械式限位开关，不带空气过滤器，24V电磁阀",1]
[2,"XV402","气动切断阀","DN125，对夹式蝶阀，-10℃，壳体：球墨铸铁，内件：304,内衬PTFE 介质：油脂，隔爆，带机械式限位开关，不带空气过滤器，24V电磁阀",1]
[3,"XV403","气动切断阀","DN125，对夹式蝶阀，-10℃，壳体：球墨铸铁，内件：304,内衬PTFE 介质：油脂，隔爆，带机械式限位开关，不带空气过滤器，24V电磁阀",1]
[4,"XV404","气动切断阀","DN125，对夹式蝶阀，-10℃，壳体：球墨铸铁，内件：304,内衬PTFE 介质：油脂，隔爆，带机械式限位开关，不带空气过滤器，24V电磁阀",1]
[5,"XVY1101","气动切断阀","DN100，对夹式双作用气动蝶阀，-10℃，壳体：球墨铸铁，内件：304, PTFE内衬 介质：油脂，隔爆，带限位开关，不带空气过滤器，24V电磁阀",1]
[6,"XVY1102","气动切断阀","DN100，对夹式双作用气动蝶阀，-10℃，壳体：球墨铸铁，内件：304, PTFE内衬 介质：油脂，隔爆，带限位开关，不带空气过滤器，24V电磁阀",1]
[7,"XVY1402","气动切断阀","DN100，对夹式双作用气动蝶阀，-10℃，壳体：球墨铸铁，内件：304, PTFE内衬 介质：油脂，隔爆，带限位开关，不带空气过滤器，24V电磁阀",1]
[8,"XVY1602","气动切断阀","DN80，对夹式双作用气动蝶阀，-10℃，壳体：球墨铸铁，内件：304, PTFE内衬 介质：油脂，隔爆，带限位开关，不带空气过滤器，24V电磁阀",1]
[9,"XVY1601","气动切断阀","DN100，对夹式双作用气动蝶阀，-10℃，壳体：球墨铸铁，内件：304, PTFE内衬 介质：油脂，隔爆，带限位开关，不带空气过滤器，24V电磁阀",1]
[10,"XVY1201","气动切断阀","DN100，对夹式双作用气动蝶阀，-10℃，壳体：球墨铸铁，内件：304, PTFE内衬 介质：油脂，隔爆，带限位开关，不带空气过滤器，24V电磁阀",1]
[11,"XVY514","气动切断阀","DN32，双作用气动球阀，碳钢，阀座石墨填充，蒸汽，160℃，，隔爆，带限位开关，不带空气过滤器，24V电磁阀",1]
[12,"XVY513","气动切断阀","DN50，双作用气动球阀，碳钢，阀座石墨填充，蒸汽，160℃，，隔爆，带限位开关，不带空气过滤器，24V电磁阀",1]
[13,"XVY514-1","气动切断阀","DN80，对夹式双作用气动蝶阀，-10℃，壳体：球墨铸铁，内件：304, PTFE内衬 介质：油脂，隔爆，带限位开关，不带空气过滤器，24V电磁阀",1]
[14,"XVY1202","气动切断阀","DN100，对夹式双作用气动蝶阀，-10℃，壳体：球墨铸铁，内件：304, PTFE内衬 介质：油脂，隔爆，带限位开关，不带空气过滤器，24V电磁阀",1]
[15,"XVY1203","气动切断阀","DN100，对夹式双作用气动蝶阀，-10℃，壳体：球墨铸铁，内件：304, PTFE内衬 介质：油脂，隔爆，带限位开关，不带空气过滤器，24V电磁阀",1]
[16,"XVY1204","气动切断阀","DN80，对夹式双作用气动蝶阀，-10℃，壳体：球墨铸铁，内件：304, PTFE内衬 介质：油脂，隔爆，带限位开关，不带空气过滤器，24V电磁阀",1]
[17,"XVY1305","气动切断阀","球阀，DN80，304,介质：油脂，隔爆，带限位开关，空气过滤器，24V电磁阀",1]
[18,"XVY1301","气动切断阀","球阀，DN80，304,介质：油脂，隔爆，带限位开关，空气过滤器，24V电磁阀",1]
[19,"XVY1304","气动切断阀","球阀，DN50，304,介质：油脂，隔爆，带限位开关，空气过滤器，24V电磁阀",1]
[20,"XVY1303","气动切断阀","球阀，DN25，304,介质：油脂，隔爆，带限位开关，空气过滤器，24V电磁阀",1]
[21,"XVY1302","气动切断阀","球阀，DN80，304,介质：油脂，隔爆，带限位开关，空气过滤器，24V电磁阀",1]
[22,"XVY1401A","气动切断阀","DN32，3片式对焊球阀，介质：压缩空气，壳体：不锈钢，内件：304，隔爆，带限位开关，空气过滤器，24V电磁阀",1]
[23,"XVY1501","气动切断阀","DN32，3片式对焊球阀，介质：压缩空气，壳体：不锈钢，内件：304，隔爆，带限位开关，空气过滤器，24V电磁阀",1]
[24,"XV01A","气动切断阀","DN80，球阀，接液材质316L，介质油脂，温度60℃，隔爆，带限位开关，空气过滤器，DC24V电磁阀，双作用",1]
[25,"XV01B","气动切断阀","DN80，球阀，接液材质316L，介质油脂，温度60℃，隔爆，带限位开关，空气过滤器，DC24V电磁阀，双作用",1]
[26,"XV02A","气动切断阀","DN80，球阀，接液材质316L，介质油脂，温度60℃，隔爆，带限位开关，空气过滤器，DC24V电磁阀，双作用",1]
[27,"XV02B","气动切断阀","DN80，球阀，接液材质316L，介质油脂，温度60℃，隔爆，带限位开关，空气过滤器，DC24V电磁阀，双作用",1]
[28,"XV03A","气动切断阀","DN80，球阀，接液材质316L，介质油脂，温度60℃，隔爆，带限位开关，空气过滤器，DC24V电磁阀，双作用",1]
[29,"XV03B","气动切断阀","DN80，球阀，接液材质316L，介质油脂，温度60℃，隔爆，带限位开关，空气过滤器，DC24V电磁阀，双作用",1]
[30,"XV2104","气动切断阀","DN50，球阀，温度：80℃，介质：酸，材质：316L，隔爆，带限位开关，空气过滤器，24v电磁阀（装消音器），双作用",1]
[31,"XV2105","气动切断阀","DN50，球阀，温度：80℃，介质：酸，材质：316L，隔爆，带限位开关，空气过滤器，24v电磁阀（装消音器），双作用",1]
[32,"XV3101","气动切断阀","DN50，球阀，温度：70℃，介质：油脂，材质：304，隔爆，带限位开关，空气过滤器，24v电磁阀（装消音器），双作用",1]
[33,"XV3102","气动切断阀","DN50，球阀，温度：70℃，介质：油脂，材质：304，隔爆，带限位开关，空气过滤器，24v电磁阀（装消音器），双作用",1]
[34,"XV813B","气动切断阀","DN20，球阀，温度：30℃，介质：压缩空气，材质：304，隔爆，带限位开关，空气过滤器，24v电磁阀（装消音器），双作用",1]
[35,"XV3103","气动切断阀","DN50，球阀，温度：70℃，介质：油脂，材质：304，隔爆，带限位开关，空气过滤器，24v电磁阀（装消音器），双作用",1]
[36,"XV3104","气动切断阀","DN50，球阀，温度：70℃，介质：油脂，材质：304，隔爆，带限位开关，空气过滤器，24v电磁阀（装消音器），双作用",1]
[37,"XV8108C","气动切断阀","DN80，球阀，温度：50℃，介质：酸，材质：316L，隔爆，带限位开关，空气过滤器，24v电磁阀（装消音器），双作用",1]
[38,"XV8109C","气动切断阀","DN80，球阀，温度：50℃，介质：酸，材质：316L，隔爆，带限位开关，空气过滤器，24v电磁阀（装消音器），双作用",1]
[39,"XV8110C","气动切断阀","DN80，球阀，温度：50℃，介质：酸，材质：316L，隔爆，带限位开关，空气过滤器，24v电磁阀（装消音器），双作用",1]
[40,"XV8111C","气动切断阀","DN80，球阀，温度：50℃，介质：酸，材质：316L，隔爆，带限位开关，空气过滤器，24v电磁阀（装消音器），双作用",1]
[41,"XV8111A","气动切断阀","DN50，球阀，温度：50℃，介质：油脂，弱酸，材质：316L，隔爆，带限位开关，空气过滤器,DC24v电磁阀（装消音器），双作用",1]
[42,"XV8111B","气动切断阀","DN50，球阀，温度：50℃，介质：油脂，弱酸，材质：316L，隔爆，带限位开关，空气过滤器,DC24v电磁阀（装消音器），双作用",1]
[43,"XV102","气动切断阀","DN100,球阀，接液材质304，介质油脂，温度50℃，EXdIIBT5，带限位开关，空气过滤器，DC24v电磁阀，双作用",1]
[44,"XV101","气动切断阀","DN20,球阀，304，介质压缩空气，温度30℃，EXdIIBT5，带限位开关，空气过滤器，DC24v电磁阀，双作用",1]
[45,"XV15","气动切断阀","DN100,球阀，接液材质304，介质油脂，温度50℃，EXdIIBT5，带限位开关，空气过滤器，DC24v电磁阀，双作用",1]
[46,"XV903","气动切断阀","DN100,球阀，接液材质304，介质油脂，温度50℃，EXdIIBT5，带限位开关，空气过滤器，DC24v电磁阀，双作用",1]
[47,"XV906","气动切断阀","DN65,球阀，接液材质304，介质油脂，温度50℃，EXdIIBT5，带限位开关，空气过滤器，DC24v电磁阀，双作用",1]
[48,"XV907","气动切断阀","DN100,球阀，接液材质304，介质油脂，温度50℃，EXdIIBT5，带限位开关，空气过滤器，DC24v电磁阀，双作用",1]
[49,"XV806","气动切断阀","DN100,球阀，接液材质304，介质油脂，温度50℃，EXdIIBT5，带限位开关，空气过滤器，DC24v电磁阀，双作用",1]
[50,"XV807","气动切断阀","DN100,球阀，接液材质304，介质油脂，温度50℃，EXdIIBT5，带限位开关，空气过滤器，DC24v电磁阀，双作用",1]
[51,"FV4109","气动调节阀","管径DN25，304，介质：植物油、甘油、甲醇，调节阀进口压力25kpa，出口压力-60kpa，温度60℃，粘度<15mm2/s,常用流量800kg/h，最小流量300kg/h，最大流量3t/h，密度900kg/m3",1]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}