{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":23,"n_cols":4,"rows_kept":23,"merged":[[1,0,7,0],[8,0,8,3],[11,0,21,0],[22,0,22,3]],"flags":["formulas_cached_only"]}
["名称","参数要求","备注","数量"]
["气动切断阀","DN32，球阀，常温，水，304，隔爆，带限位开关，空气过滤器，DC24V电磁阀（带消音器），",null,1]
[]
[null,"DN50，球阀，常温，甲醇，304，隔爆，带限位开关，空气过滤器，DC24V电磁阀（带消音器），双作用",null,1]
[]
[null,"DN80，球阀，接液材质304衬氟，油脂，盐酸，温度≦80℃，隔爆，带限位开关，空气过滤器，DC24V电磁阀，双作用",null,1]
[]
[null,"DN80，球阀，接液材质304衬氟，油脂，盐酸，温度≦80℃，隔爆，带限位开关，空气过滤器，DC24V电磁阀，双作用",null,1]
["备注：电磁阀带接线盒"]
[]
[]
["气动调节阀","DN50，常用流量：1t/h,蒸汽，阀前压力0.6Mpa,阀后压力0.3MPa，140℃，阀体WCB,阀芯304，隔爆，带机械型定位器，减压过滤器，气开型",null,1]
[]
[null,"DN50，常用流量，10m³/h,，最大流量15m³/h,油脂，酸，阀前压力0.2Mpa,120℃，304衬FPA，隔爆，带机械型定位器，减压过滤器，气开型",null,1]
[]
[null,"DN25，甲醇，常温，800kg/m³，最小/常用/最大流量：0/1.2/3m³/h,最小流量时压力：阀前0.3，阀后0.2MPa,气源0.6MPa，管道DN25,\n304，PN16，要求：量程0~100%，EXdIIBT4,带三联件，阀体/内件：304，电器接口M20*1.5，带机械型定位器，4-20mA，不需要阀门反馈及手轮，失气关",null,1]
[]
[null,"DN40，常用流量0.6t/h,蒸汽，阀前压力：0.6MPa，阀后压力：0.3MPa，温度;140℃,阀体/阀芯：碳钢/304，隔爆，带机械型定位器，减压过滤器，气开型",null,1]
[]
[null,"DN25，甲醇，常温，800kg/m³，最小/常用/最大流量：0/1.2/3m³/h,最小流量时压力：阀前0.15MPa，阀后0.05MPa,气源0.6MPa，管道DN25,\n304，PN16，要求：量程0~100%，EXdIIBT4,带三联件，阀体/内件：304，电器接口M20*1.5，带机械型定位器，4-20mA，不需要阀门反馈及手轮，失气关",null,1]
[]
[null,"DN65，常用流量15m³/h,最大流量25m³/h,水，阀前压力：0.15MPa，阀后压力：0MPa，温度:常温,阀体/阀芯：碳钢/304，隔爆，带机械型定位器，减压过滤器，气开型",null,1]
["备注：定位器指定品牌韩国永泰YT1000"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}