{"text_format":"3","workbook":"xlsx","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":25,"n_cols":3,"rows_kept":25,"merged":[[6,0,11,0],[12,0,18,0],[19,0,24,0]]}
["序号","要求","备注"]
["螺旋板厚度","详见附件条件图"]
["换热器材质","详见附件条件图"]
["不锈钢板材","宝钢、太钢、东特、张浦或同等（容器板，板厚偏差+/-0.25），需提供材料供应商原始质量检验合格证书，发票、合同等有关文件"]
["设计、制作标准","按照JB/T4751-2003《螺旋板式换热器》设计、制造、检验；换热器主要受压原件材料选用应符合GB/150-1998第4章“材料”规定"]
["焊接要求","1.焊缝和热影响区表面不得有裂纹、气孔、弧坑和夹渣等缺陷；\n2.两通道间的连接圆钢，应采用两点对称点焊；\n3.＞15㎡螺旋板采用两端面交替施焊；\n4.焊接时由螺旋板中心向外施焊；\n5.焊缝与母材需圆滑过渡；\n6.焊缝打磨后的厚度不能小于母材厚度；\n7.焊缝上的熔渣和两侧飞溅物需清理干净；\n"]
["制作要求","1、螺旋板的卷筒板及薄板选用应符合GB/T192、GB/T3280、GB/T4237、GB/T4239、YB/T5090的规定选用，并附钢厂质量证明书，同时还应符合《压力容器安全技术监察规程》的规定，且要求不锈钢板厚≥2mm，碳钢板厚度≥3mm；条件图中厚度已有要求的以条件图中厚度为准"]
[null,"2、接管材料按GB/T8163、GB13296、GB/T14976的规定选用，并附质量证明书"]
[null,"3、焊接材料应按GB/T983、GB/T5117、GB/T5118的规定选用，并附质量证明书"]
[null,"4、管口方位严格按照我方提供的设备管口方位图开孔制作，管口大小根据设计可能会略有改动。"]
[null,"5、设备铭牌采用S30408不锈钢材质制作。"]
[null,"6、设备制作完毕后内壁需清扫干净，所有管口打盲板密封，防雨水或潮气进入，设备需用微正压氮气进行密封交货。"]
["供货范围","1. 设备本体及内件"]
[null,"2. 设备本体连接用螺栓, 螺母及垫片；"]
[null,"3. 铭牌及铭牌支架"]
[null,"4. 设备材料及制作、标准件采购、非标准外购件的采购及安装调试、水压试验、无损检验、防腐等均在供货范围之内"]
[null,"5. 现场安装及维修专用工具（如有）"]
[null,"6. 仪表口、排气口、排液口、检漏口、备用扣等配法兰盖及所配螺栓, 螺母及垫片"]
[null,"7. 配备管口配对法兰、垫片及螺栓紧固件。"]
["卖方工作范围","1. 设备材料进厂复验、设备制造、检验和试验"]
[null,"2. 制定焊接工艺规程，设备的预组装试验"]
[null,"3. 不锈钢部分的酸洗、钝化处理"]
[null,"4. 制造、运输、储存时设备内部保护"]
[null,"5. 运输包装"]
[null,"6. 现场指导安装"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0}