{"text_format":"3","workbook":"xlsx","n_sheets":4,"sheets":["压力","温度","单法兰液位变送器","双法兰差压变送器"],"not_rendered":{"defined_names":4},"read":"whole","date_system":"1900"}

{"sheet":"压力","index":0,"n_rows":174,"n_cols":28,"rows_kept":174,"merged":[[173,19,173,20]]}
["备注","类别","序号","工段/部门","位号","新位号","仪表名称","测点","介质","设计温度/℃","实际工作压力","是否配置冷凝圈","量程/Mpa/kpa","过程连接形式及尺寸","法兰标准及压力等级","接液材质","毛细管长度/m","安装支架","精度要求/%/pa","防爆/防护等级","电气接口","供电电压","接线制","信号传输","现场显示","数量/个/台","生产厂家","备注"]
[null,"B",1,"11a","PI2117","PICA2117","隔膜压力变送器","一号线2号釜转料泵出口压力1","油脂，酸",110,"0.3mpa","否","0-1.6MPa","DN25","HG20592-09，PN16","316L+PFA","1m","是",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",2,"11a","PI2118","PICA2118","隔膜压力变送器","一号线1号釜转料泵出口压力1","油脂，酸",105,"0.3mpa","否","0-1.6MPa","DN25","HG20592-09，PN16","316L+PFA","1m","是",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",3,"11a","PI2121","PICA2121","隔膜压力变送器","一号线4号釜转料泵出口压力1","油脂，酸",80,"0.3mpa","否","0-1.6MPa","DN25","HG20592-09，PN16","316L+PFA","1m","是",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",4,"11a","PI2126","PICA2126","隔膜压力变送器","一号线3号釜转料泵出口压力1","油脂，酸",115,"0.3mpa","否","0-1.6MPa","DN25","HG20592-09，PN16","316L+PFA","1m","是",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",5,"11a","PI2214","PICA2214","隔膜压力变送器","一号线2号釜转料泵出口压力2","油脂，酸",110,"0.3mpa","否","0-1.6MPa","DN25","HG20592-09，PN16","316L+PFA","1m","是",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",6,"11a","PI2216","PICA2216","隔膜压力变送器","一号线1号釜转料泵出口压力2","油脂，酸",105,"0.3mpa","否","0-1.6MPa","DN25","HG20592-09，PN16","316L+PFA","1m","是",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",7,"11a","PI2219","PICA2219","隔膜压力变送器","一号线4号釜转料泵出口压力2","油脂，酸",80,"0.3mpa","否","0-1.6MPa","DN25","HG20592-09，PN16","316L+PFA","1m","是",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",8,"11a","PI2222","PICA2222","隔膜压力变送器","一号线3号釜转料泵出口压力2","油脂，酸",115,"0.3mpa","否","0-1.6MPa","DN25","HG20592-09，PN16","316L+PFA","1m","是",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",9,"11a","PI6101",null,"压力变送器","V6101罐压力","甲醇",30,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",10,"11a","PI6201",null,"压力变送器","V6201罐压力","甲醇",30,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",11,"11a","PI7105",null,"压力变送器","T-7101加热蒸汽压力","蒸汽",150,"0.3mpa","是","0-1.0Mpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",12,"11a","PI7107",null,"隔膜压力变送器","P7106泵口压力","油脂，酸",50,"0.2mpa","否","0-1.6MPa","DN25","HG20592-09，PN16","316L+PFA","1m","是",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",13,"11a","PIA2107",null,"绝压变送器","冷却釜R-2104压力","甲醇，油脂，酸",100,"40kpa","否","0-300KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",14,"11a","PIA2109",null,"压力变送器","甲醇加热器出口压力","甲醇",90,"0.2mpa","否","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",15,"11a","PIA2111",null,"压力变送器","分酸罐V-2106压力","油脂，酸",80,"1kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",16,"11a","PIA2112",null,"压力变送器","分酸罐V-2107压力","油脂，酸",80,"1kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",17,"11a","PIA2127",null,"压力变送器","甲醇缓冲槽V-2102压力","甲醇","常温","1kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",18,"11a","PIA2207",null,"绝压变送器","冷却釜R-2204压力","甲醇，油脂，酸",100,"40kpa","否","0-300KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",19,"11a","PIA2209",null,"压力变送器","甲醇加热器出口压力","甲醇",90,"0.2mpa","否","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",20,"11a","PIA3101",null,"压力变送器","酯交换加热器E-3101蒸汽管线压力","蒸汽",180,"0.1mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",21,"11a","PIA3102",null,"压力变送器","酯交换加热器E-3102蒸汽管线压力","蒸汽",180,"0.1mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",22,"11a","PIA3119",null,"压力变送器","V3102罐压力","甲醇",35,"1kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",23,"11a","PIA3120",null,"压力变送器","V3104罐压力","甲醇",35,"1kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",24,"11a","PIA4101",null,"压力变送器","脱醇加热器E-4101蒸汽管线压力","蒸汽",180,"0.2mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",25,"11a","PIA4102",null,"绝压变送器","脱醇塔T-4101顶部压力","甲醇",100,"40kpa","否","0-300KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",26,"11a","PIA4103",null,"压力变送器","脱醇塔T-4101塔釜蒸汽管线压力","蒸汽",180,"0.2mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",27,"11a","PIA6101",null,"压力变送器","甲醇塔T-6101顶部压力","甲醇",100,"3kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",28,"11a","PIA6102",null,"压力变送器","甲醇塔T-6101中部压力","甲醇",100,"3kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",29,"11a","PIA6103",null,"压力变送器","甲醇塔T-6101底部压力","甲醇水",100,"3kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",30,"11a","PIA6105",null,"压力变送器","甲醇塔釜R-6101蒸汽管线压力","蒸汽",180,"0.2mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",31,"11a","PIA6201",null,"压力变送器","甲醇塔T-6201顶部压力","甲醇",100,"3kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",32,"11a","PIA6202",null,"压力变送器","甲醇塔T-6201中部压力","甲醇",100,"3kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",33,"11a","PIA6203",null,"压力变送器","甲醇塔T-6201底部压力","甲醇水",100,"3kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",34,"11a","PIA6205",null,"压力变送器","甲醇塔釜R-6201蒸汽管线压力","蒸汽",180,"0.2mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",35,"11a","PIA7101",null,"绝压变送器","脱醇塔T-7101塔顶压力","甲醇",110,"40kpa","否","0-300KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",36,"11a","PIA7102",null,"压力变送器","脱醇加热器E-7101蒸汽管线压力","蒸汽",180,"0.2mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",37,"11a","PIA7103",null,"压力变送器","R7101罐压力","油脂，酸",35,"1kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",38,"11a","PIA7104",null,"隔膜压力变送器","1020进料泵P-7103出口压力","油脂，酸",60,"0.2mpa","否","0-1.6MPa","DN25","HG20592-09，PN16","316L+PFA","1m","是",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",39,"11a","PIA9201",null,"压力变送器","冷冻水总管压力","水，乙二醇",-10,"0.2mpa","否","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",40,"11a","PIA9301",null,"压力变送器","循环水上水总管压力","水",28,"0.2mpa","否","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",41,"11a","PIA9302",null,"压力变送器","循环水回水总管压力","水",30,null,"否","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",42,"11a","PIA9401",null,"压力变送器","厂区总蒸汽进气压力","蒸汽",220,"1mpa","是","0-1.6MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",43,"11a","PIA9402",null,"压力变送器","蒸汽冷凝水去收集罐总管压力","水",90,"0.2mpa","否","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",44,"11a","PIA9403",null,"压力变送器","蒸汽支总管压力","蒸汽",180,"0.6mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",45,"11a","PIA9404",null,"压力变送器","蒸汽支总管压力","蒸汽",180,"0.6mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",46,"11a","PIA9405",null,"压力变送器","蒸汽支总管去罐区压力","蒸汽",180,"0.6mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",47,"11a","PIA9406",null,"压力变送器","蒸汽支总管去工业级混合油压力","蒸汽",180,"0.6mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",48,"11a","PIA9501",null,"压力变送器","氮气缓冲罐压力","氮气","常温","0.6mpa","否","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",49,"11a","PIA9601",null,"压力变送器","压缩空气包压力","空气","常温","0.6mpa","否","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1,null,"pid需调整"]
[null,"B",50,"11a","PIA9602",null,"压力变送器","一号线压缩空气管末端压力","空气","常温","0.6mpa","否","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1,null,"pid需调整"]
[null,"B",51,"11a","PIA9603",null,"压力变送器","二号线压缩空气管末端压力","空气","常温","0.6mpa","否","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1,null,"pid需调整"]
[null,"B",52,"11a","PIA9604",null,"压力变送器","罐区压缩空气管末端压力","空气","常温","0.6mpa","否","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1,null,"pid需调整"]
[null,"B",53,"11a","PICA1103",null,"压力变送器","原料预热器蒸汽进口管线压力","蒸汽",180,"0.2mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",54,"11a","PICA2101",null,"压力变送器","反应釜R-2101夹套蒸汽管线压力","蒸汽",180,"0.1mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",55,"11a","PICA2102",null,"压力变送器","反应釜R-2102夹套蒸汽管线压力","蒸汽",180,"0.1mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",56,"11a","PICA2103",null,"压力变送器","反应釜R-2103夹套蒸汽管线压力","蒸汽",180,"0.1mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",57,"11a","PICA2108",null,"压力变送器","甲醇加热器蒸汽管线压力","蒸汽",180,"0.3mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",58,"11a","PICA2201",null,"压力变送器","反应釜R-2201夹套蒸汽管线压力","蒸汽",180,"0.1mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",59,"11a","PICA2202",null,"压力变送器","反应釜R-2202夹套蒸汽管线压力","蒸汽",180,"0.1mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",60,"11a","PICA2203",null,"压力变送器","反应釜R-2203夹套蒸汽管线压力","蒸汽",180,"0.1mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",61,"11a","PICA2208",null,"压力变送器","甲醇加热器蒸汽管线压力","蒸汽",180,"0.3mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",62,"11a","PICA6106",null,"压力变送器","甲醇塔釜R-6102蒸汽管线压力","蒸汽",180,"0.3mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",63,"11a","PICA6206",null,"压力变送器","甲醇塔釜R-6202蒸汽管线压力","蒸汽",180,"0.3mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",64,"11a","PISA2104",null,"隔膜压力变送器","反应釜R-2101压力","甲醇，油脂，酸",150,"0.01mpa","是","0-1.0MPa","DN50","HG20592-09，PN16","316L","1.5m","是",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",65,"11a","PISA2105",null,"隔膜压力变送器","反应釜R-2102压力","甲醇，油脂，酸",150,"0.1mpa","是","0-1.0MPa","DN50","HG20592-09，PN16","316L","1.5m","是",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",66,"11a","PISA2106",null,"隔膜压力变送器","反应釜R-2103压力","甲醇，油脂，酸",150,"0.16mpa","是","0-1.0MPa","DN50","HG20592-09，PN16","316L","1.5m","是",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",67,"11a","PISA2204",null,"隔膜压力变送器","反应釜R-2201压力","甲醇，油脂，酸",150,"0.01mpa","是","0-1.0MPa","DN50","HG20592-09，PN16","316L","1.5m","是",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",68,"11a","PISA2205",null,"隔膜压力变送器","反应釜R-2202压力","甲醇，油脂，酸",150,"0.1mpa","是","0-1.0MPa","DN50","HG20592-09，PN16","316L","1.5m","是",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",69,"11a","PISA2206",null,"隔膜压力变送器","反应釜R-2203压力","甲醇，油脂，酸",150,"0.16mpa","是","0-1.0MPa","DN50","HG20592-09，PN16","316L","1.5m","是",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",70,"11a","PISA3103",null,"绝压变送器","酯交换一反应器压力","油脂",70,null,"否","0-300KPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",71,"11a","PISA3104",null,"绝压变送器","酯交换二反应器压力","油脂",70,null,"否","0-300KPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",72,"11c","PIA5101",null,"绝压变送器","闪蒸塔T5101塔顶真空","油脂",150,"0.3kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",73,"11c","PIA5202",null,"绝压变送器","脱臭塔T5201塔中真空","油脂",200,"0.4kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",74,"11c","PIA5203",null,"绝压变送器","脱臭塔T5201塔中真空","油脂",200,"0.4kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",75,"11c","PIA5204",null,"绝压变送器","脱臭塔T5201塔底真空","油脂",250,"0.5kpa","是","0-300KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",76,"11c","PIA5205",null,"绝压变送器","V5201接收罐真空","油脂",200,"0.2kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",77,"11c","PIA5208",null,"绝压变送器","V5202尾冷接收罐真空","油脂",100,"0.2kpa","否","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",78,"11c","PIA5209","PICA5209","压力变送器","V5203蒸汽包压力","蒸汽",180,"0.2mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",79,"11c","PIA5302",null,"绝压变送器","16塔T5301塔中真空","油脂",200,"0.4kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",80,"11c","PIA5303",null,"绝压变送器","16塔T5301塔中真空","油脂",200,"0.4kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",81,"11c","PIA5304",null,"绝压变送器","16塔T5301塔中真空","油脂",200,"0.4kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",82,"11c","PIA5305",null,"绝压变送器","16塔T5301塔底真空","油脂",250,"0.5kpa","是","0-300KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",83,"11c","PIA5306",null,"绝压变送器","V5301接收罐真空","油脂",200,"0.2kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",84,"11c","PIA5309",null,"绝压变送器","V5302尾冷接收罐真空","油脂",100,"0.2kpa","否","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",85,"11c","PIA5310",null,"绝压变送器","V5304真空缓冲罐真空","油脂",100,"0.2kpa","否","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",86,"11c","PIA5311",null,"绝压变送器","V5305接收罐真空","油脂",200,"0.2kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",87,"11c","PIA5402",null,"绝压变送器","18塔T5401塔中真空","油脂",200,"0.4kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",88,"11c","PIA5403",null,"绝压变送器","18塔T5401塔中真空","油脂",200,"0.4kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",89,"11c","PIA5404",null,"绝压变送器","18塔T5401塔底真空","油脂",250,"0.5kpa","是","0-300KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",90,"11c","PIA5405",null,"绝压变送器","V5402接收罐真空","油脂",200,"1kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",91,"11c","PIA5406",null,"绝压变送器","V5401接收罐真空","油脂",200,"0.2kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",92,"11c","PIA5407",null,"绝压变送器","V5403尾冷接收罐真空","油脂",100,"0.2kpa","否","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",93,"11c","PIA5411","PICA5411","压力变送器","V5405蒸汽包压力","蒸汽",180,"0.2mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",94,"11c","PIA5412",null,"绝压变送器","V5404真空缓冲罐真空","油脂",100,"0.2kpa","否","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",95,"11c","PIA5414",null,"绝压变送器","3#真空机组真空","甲醇",50,"0.3kpa","否","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",96,"11c","PIA5415",null,"压力变送器","1010储罐V5407压力","油脂",100,null,"否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",97,"11c","PIA8502",null,"绝压变送器","复蒸塔中部真空","油脂",200,"0.4kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",98,"11c","PIA8503",null,"绝压变送器","复蒸塔中部真空","油脂",200,"0.4kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",99,"11c","PIA8504",null,"绝压变送器","复蒸塔底部真空","油脂",250,"0.5kpa","是","0-300KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",100,"11c","PIA8505",null,"绝压变送器","V8502接收罐真空","油脂",200,"0.2kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",101,"11c","PIA8506",null,"绝压变送器","V8501接收罐真空","油脂",200,"0.2kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",102,"11c","PIA8507",null,"绝压变送器","V8503尾冷接收罐真空","油脂",100,"0.2kpa","否","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",103,"11c","PIA8508",null,"绝压变送器","V8504真空缓冲罐真空","油脂",100,"0.2kpa","否","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",104,"11c","PIA8509","PICA8509","压力变送器","V8505蒸汽包压力","蒸汽",180,"0.2mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",105,"11c","PIA8602",null,"绝压变送器","沥青塔T8601塔底真空","油脂",250,"0.5kpa","是","0-300KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",106,"11c","PIA8603",null,"绝压变送器","V8601接收罐真空","油脂",200,"0.2kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",107,"11c","PIA9011",null,"压力变送器","导热油总管进油压力","导热油",280,"0.3mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",108,"11c","PIA9012",null,"压力变送器","导热油总管回油压力","导热油",270,null,"是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",109,"11c","PIA9013",null,"压力变送器","氮气总管进气压力","氮气",20,"0.6mpa","否","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",110,"11c","PICA5312",null,"绝压变送器","1#真空机组真空","甲醇",50,"0.3kpa","否","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",111,"11c","PICA5410",null,"压力变送器","蒸汽包管道压力","蒸汽",180,"0.2mpa","是","0-1.0MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",112,"11c","PICA5413",null,"绝压变送器","2#真空机组真空","甲醇",50,"0.3kpa","否","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",113,"11c","PICA8510",null,"绝压变送器","4#真空机组真空","甲醇",50,"0.3kpa","否","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",114,"11c","PICA8511",null,"绝压变送器","5#真空机组真空","甲醇",50,"0.3kpa","否","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",115,"11c","PICA8512",null,"压力变送器","1010储罐V8507压力","油脂",100,null,"否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",116,"11c","PISA5201","PICSA5201","绝压变送器","脱臭塔T5201塔顶真空","油脂",200,"0.3kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",117,"11c","PISA5301","PICSA5301","绝压变送器","16塔T5301塔顶真空","油脂",200,"0.3kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",118,"11c","PISA5401","PICSA5401","绝压变送器","18塔T5401塔顶真空","油脂",200,"0.3kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",119,"11c","PISA8501","PICSA8501","绝压变送器","复蒸塔T8501塔顶真空","油脂",200,"0.3kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",120,"11c","PISA8601","PICSA8601","绝压变送器","沥青塔T8601塔顶真空","油脂",200,"0.3kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",121,13,"PIA301A",null,"压力变送器","1#搅拌釜压力","油脂","常温","0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",122,13,"PIA302A",null,"压力变送器","2#搅拌釜压力","油脂","常温","0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",123,13,"PIA303A",null,"压力变送器","3#暂存釜压力","油脂","常温","0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",124,13,"PIA304A",null,"压力变送器","4#暂存釜压力","油脂","常温","0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",125,41,"PIATK101B","PISATK101B","压力变送器","TK101顶部压力","盐酸，油脂，甘油",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",126,41,"PIATK104B","PISATK104B","压力变送器","TK104顶部压力","盐酸，油脂，甘油",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",127,41,"PIATK105B","PISATK105B","压力变送器","TK105顶部压力","盐酸，油脂，甘油",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",128,41,"PIATK106B","PISATK106B","压力变送器","TK106顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",129,41,"PIATK107B","PISATK107B","压力变送器","TK107顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",130,41,"PIATK108B","PISATK108B","压力变送器","TK108顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",131,41,"PIATK109B","PISATK109B","压力变送器","TK109顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",132,41,"PIATK110B","PISATK110B","压力变送器","TK110顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",133,41,"PIATK111B","PISATK111B","压力变送器","TK111顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",134,41,"PIATK112B","PISATK112B","压力变送器","TK112顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",135,41,"PIATK113B","PISATK113B","压力变送器","TK113顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",136,41,"PIATK114B","PISATK114B","压力变送器","TK114顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",137,41,"PIATK115B","PISATK115B","压力变送器","TK115顶部压力","水",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",138,41,"PIATK116B","PISATK116B","压力变送器","TK116顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",139,41,"PIATK117B","PISATK117B","压力变送器","TK117顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",140,41,"PIATK118B","PISATK118B","压力变送器","TK118顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",141,41,"PIATK119B","PISATK119B","压力变送器","TK119顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",142,41,"PIATK120B","PISATK120B","压力变送器","TK120顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",143,41,"PIATK121B","PISATK121B","压力变送器","TK121顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",144,41,"PIATK122B","PISATK122B","压力变送器","TK122顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",145,41,"PIATK123B","PISATK123B","压力变送器","TK123顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",146,41,"PIATK124B","PISATK124B","压力变送器","TK124顶部压力","油脂",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",147,41,"PIATK125B","PISATK125B","压力变送器","TK125顶部压力","甲醇","常温","0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",148,41,"PIATK126B","PISATK126B","压力变送器","TK126顶部压力","甲醇","常温","0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",149,41,"PIATK127B","PISATK127B","压力变送器","TK127顶部压力","盐酸",35,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",150,41,"PITK102B","PISATK102B","压力变送器","TK102顶部压力","废酸",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",151,41,"PITK103B","PISATK103B","压力变送器","TK103顶部压力","水",50,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",152,"备件","BYPI1601",null,"压力变送器","/","油脂",100,"0.2mpa","否","0-1.6MPa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",153,"备件","BYPI1001",null,"压力变送器","/","油脂",100,"0.2mpa","否","0-1.0Mpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",154,"备件","BYPI1002",null,"压力变送器","/","油脂",100,"0.2mpa","否","0-1.0Mpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",155,"备件","BYPI1003",null,"压力变送器","/","油脂",100,"0.2mpa","否","0-1.0Mpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",156,"备件","BYPI1004",null,"压力变送器","/","油脂",100,"0.2mpa","否","0-1.0Mpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",157,"备件","BYPI1005",null,"压力变送器","/","油脂",100,"0.2mpa","否","0-1.0Mpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",158,"备件","BYPI3001",null,"绝压变送器","/","油脂",200,"0.3kpa","是","0-300KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",159,"备件","BYPI1301",null,"绝压变送器","/","油脂",250,"0.3kpa","是","0-300KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",160,"备件","BYPI0001",null,"压力变送器","/","油脂",100,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",161,"备件","BYPI0002",null,"压力变送器","/","油脂",100,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",162,"备件","BYPI0003",null,"压力变送器","/","油脂",100,"0.5kpa","否","-10~10Kpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",163,"备件","BYPI2001",null,"绝压变送器","/","油脂",200,"0.3kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",164,"备件","BYPI2002",null,"绝压变送器","/","油脂",200,"0.3kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"A",165,"备件","BYPI2003",null,"绝压变送器","/","油脂",200,"0.3kpa","是","0-20KPa","M20*1.5","/","316L","/","否","100pa","EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",166,"备件","BYPI1602",null,"隔膜压力变送器","/","油脂，酸",100,"0.3mpa","否","0-1.6MPa","DN25","HG20592-09，PN16","316L","1m","是",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[null,"B",167,"备件","BYPI1006",null,"隔膜压力变送器","/","油脂，酸",100,"0.1mpa","否","0-1.0Mpa","DN50","HG20592-09，PN16","316L","1.5m","是",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
["新增","B",168,"11c","PICSA5102",null,"压力变送器","T-5101加热蒸汽压力","蒸汽",150,"0.3mpa","是","0-1.0Mpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
["新增","B",169,"11a","PI7106",null,"压力变送器","R7101蒸汽压力","蒸汽",150,"0.2mpa","是","0-1.0Mpa","M20*1.5","/","316L","/","否",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
["新增","B",170,41,"PICP424B",null,"压力变送器","P424泵出口压力指示","油脂",80,"0.3mpa","否","0-1.0Mpa","DN25","/","316L","1m","是",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
["新增","B",171,41,"PICP423B2",null,"压力变送器","P423B泵出口压力指示","油脂",80,"0.3mpa","否","0-1.0Mpa","DN25","/","316L","1m","是",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
["新增","B",172,41,"PICP423A2",null,"压力变送器","P423A泵出口压力指示","油脂",80,"0.3mpa","否","0-1.0Mpa","DN25","/","316L","1m","是",0.1,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","LCD",1]
[{"$nulls":19},"合计",null,{"$f":"SUM(V2:V173)","v":0}]

{"sheet":"温度","index":1,"n_rows":222,"n_cols":24,"rows_kept":222}
["序号","新位号","仪表名称","测点","介质","工作压力/MPa","量程范围/℃","插深（包含螺纹）/mm","保护管直径/φmm","过程连接形式及尺寸（螺纹连接配双金属底座）","法兰标准及压力等级","接液材质","传感器类型","精度要求/%","防爆/防护等级","电气接口","供电电压","输出接线","信号传输","现场显示","数量/个/台","申购日期","生产厂家","备注"]
[1,null,"温度变送器","罐区进车间原料温度","油脂，酸","<0.3","0-200",150,"⌀16","M27*2","/","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[2,"TICA2111B","温度变送器","E2106物料冷凝器出料温度","甲醇，油脂，酸","<0.3","0-200",150,"⌀16","M27*2","/","钛","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[3,null,"温度变送器","E3101出口温度","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[4,null,"温度变送器","E3102出口温度","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[5,null,"温度变送器","T-6101回流温度","甲醇","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[6,null,"温度变送器","T-6102回流温度","甲醇","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[7,null,"温度变送器","T-7101加热蒸汽排水温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[8,null,"温度变送器","原料换热器E-1110出口温度","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[9,null,"温度变送器","原料换热器E-1109出口温度","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[10,null,"温度变送器","原料预热器出口温度","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[11,null,"温度变送器","原料预热器蒸汽冷凝水出口温度","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[12,null,"温度变送器","反应釜R-2101蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[13,null,"温度变送器","反应釜R-2102蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[14,null,"温度变送器","反应釜R-2103蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[15,null,"温度变送器","甲醇加热器出口温度","甲醇","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[16,null,"温度变送器","甲醇加热器蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[17,null,"温度变送器","甲醇冷凝器E-2103不凝气出口温度","甲醇","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[18,null,"温度变送器","甲醇接收罐V-2104温度","甲醇","<0.3","0-200",400,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[19,null,"温度变送器","反应釜R-2101出料温度","甲醇，油脂，酸","<0.3","0-200",150,"⌀16","DN25","HG20592-09，PN16","钛","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[20,null,"温度变送器","反应釜R-2102出料温度","甲醇，油脂，酸","<0.3","0-200",150,"⌀16","DN25","HG20592-09，PN16","钛","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[21,null,"温度变送器","反应釜R-2103出料温度","甲醇，油脂，酸","<0.3","0-200",150,"⌀16","DN25","HG20592-09，PN16","钛","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[22,null,"温度变送器","冷却釜R-2104出料温度","甲醇，油脂，酸","<0.3","0-200",150,"⌀16","DN25","HG20592-09，PN16","钛","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[23,null,"温度变送器","反应釜R-2201蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[24,null,"温度变送器","反应釜R-2202蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[25,null,"温度变送器","反应釜R-2203蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[26,null,"温度变送器","甲醇加热器出口温度","甲醇","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[27,null,"温度变送器","甲醇加热器蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[28,null,"温度变送器","甲醇冷凝器E-2203不凝气出口温度","甲醇","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[29,null,"温度变送器","甲醇接收罐V-2204温度","甲醇","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[30,null,"温度变送器","反应釜R-2201出料温度","甲醇，油脂，酸","<0.3","0-200",150,"⌀16","DN25","HG20592-09，PN16","钛","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[31,null,"温度变送器","反应釜R-2202出料温度","甲醇，油脂，酸","<0.3","0-200",150,"⌀16","DN25","HG20592-09，PN16","钛","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[32,null,"温度变送器","反应釜R-2203出料温度","甲醇，油脂，酸","<0.3","0-200",150,"⌀16","DN25","HG20592-09，PN16","钛","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[33,null,"温度变送器","冷却釜R-2204出料温度","甲醇，油脂，酸","<0.3","0-200",150,"⌀16","DN25","HG20592-09，PN16","钛","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[34,null,"温度变送器","醇碱釜V-3102温度","甲醇，KOH","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[35,null,"温度变送器","醇碱釜V-3103温度","甲醇，KOH","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[36,null,"温度变送器","酯交换加热器E-3101蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[37,null,"温度变送器","酯交换加热器E-3102蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[38,null,"温度变送器","物料换热器E-4107出口温度","甲醇，油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[39,null,"温度变送器","甲醇接收罐V-4105温度","甲醇","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[40,null,"温度变送器","物料换热器E-4107壳程出口管线温度","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[41,null,"温度变送器","甲醇冷凝器E-4105出口温度","甲醇","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[42,null,"温度变送器","脱醇加热器E-4101蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[43,null,"温度变送器","甲醇塔T-4101塔釜蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[44,null,"温度变送器","甲醇塔釜R-6101蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[45,null,"温度变送器","甲醇塔釜R-6102蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[46,null,"温度变送器","T6101塔釜温度","水，甲醇","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[47,null,"温度变送器","甲醇接收罐V-6101温度","甲醇","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[48,null,"温度变送器","甲醇塔釜R-6201蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[49,null,"温度变送器","甲醇塔釜R-6202蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[50,null,"温度变送器","T6201塔釜温度","水，甲醇","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[51,null,"温度变送器","甲醇接收罐V-6201温度","甲醇","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[52,null,"温度变送器","甲醇冷凝器E-7103壳程出口温度","甲醇","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[53,null,"温度变送器","脱醇塔T-7101塔底出口温度","甘油","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[54,null,"温度变送器","脱醇加热器E-7101蒸汽冷凝水出口温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[55,null,"温度变送器","1020处理釜温度","空气","<0.3","0-200",3300,"⌀6","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[56,null,"温度变送器","放空冷凝器E-7104出口温度","甲醇","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[57,null,"温度变送器","甲醇收集罐V-7101温度","甲醇","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[58,null,"温度变送器","冷冻水上水总管温度","冷冻水","<0.3","-20~100",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[59,null,"温度变送器","冷冻水回水总管温度","冷冻水","<0.3","-20~100",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[60,null,"温度变送器","循环水上水总管温度","水","<0.3","0-200",400,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[61,null,"温度变送器","循环水回水总管温度","水","<0.3","0-200",400,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[62,null,"温度变送器","东侧循环水回水支总管温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[63,null,"温度变送器","西侧循环水回水支总管温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[64,null,"温度变送器","厂区总蒸汽进气温度","蒸汽","<0.3","0-300",200,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[65,null,"温度变送器","蒸汽冷凝水总管温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[66,null,"温度变送器","蒸汽支总管温度","蒸汽","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[67,null,"温度变送器","蒸汽支总管温度","蒸汽","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[68,null,"温度变送器","蒸汽支总管去罐区温度","蒸汽","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[69,null,"温度变送器","蒸汽支总管去工业级混合油温度","蒸汽","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[70,null,"温度变送器","蒸汽冷凝水收集罐温度","水","<0.3","0-200",400,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[71,null,"温度变送器","车间废气进气温度","甲醇，酸","<0.3","0-200",150,"⌀16","M27*2","/","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[72,null,"温度变送器","废气一级冷凝后温度","甲醇，酸","<0.3","0-200",150,"⌀16","M27*2","/","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[73,null,"温度变送器","废气二级冷凝后温度","甲醇，酸","<0.3","0-200",150,"⌀16","M27*2","/","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[74,null,"温度变送器","尾气塔一温度","甲醇，酸","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[75,null,"温度变送器","尾气塔二温度","甲醇，酸","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[76,null,"温度变送器","热水罐温度","水","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[77,null,"温度变送器","冷却釜R-2104温度","空气","<0.3","0-200",2900,"⌀6","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[78,null,"温度变送器","E2104物料冷凝器出口温度","甲醇，油脂，酸","<0.3","0-200",150,"⌀16","M27*2","/","钛","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[79,null,"温度变送器","冷却釜R-2204温度","空气","<0.3","0-200",2900,"⌀6","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[80,null,"温度变送器","脱醇加热器E-4101出口温度","甲醇，油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[81,null,"温度变送器","甲醇塔T-6101顶部温度","甲醇","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[82,null,"温度变送器","甲醇塔T-6201顶部温度","甲醇","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[83,null,"温度变送器","脱醇加热器E-7101出口温度","甲醇，甘油","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[84,null,"温度变送器","酯交换一反应器温度","甲醇，油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[85,null,"温度变送器","酯交换二反应器温度","甲醇，油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[86,null,"温度变送器","脱醇塔T-4101塔釜出料温度","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[87,null,"温度变送器","反应釜R-2101温度","空气","<0.3","0-200",3300,"⌀6","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[88,null,"温度变送器","反应釜R-2102温度","空气","<0.3","0-200",3600,"⌀6","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[89,null,"温度变送器","反应釜R-2103温度","空气","<0.3","0-200",3600,"⌀6","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[90,null,"温度变送器","反应釜R-2201温度","空气","<0.3","0-200",3300,"⌀6","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[91,null,"温度变送器","反应釜R-2202温度","空气","<0.3","0-200",3600,"⌀6","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[92,null,"温度变送器","反应釜R-2203温度","空气","<0.3","0-200",3600,"⌀6","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[93,null,"温度变送器","R6102出水温度","水，甲醇","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[94,null,"温度变送器","R6202出水温度","水，甲醇","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[95,null,"温度变送器","T-5101蒸汽排水温度","水","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[96,"TIA5211","温度变送器","P5201进口温度","油脂","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[97,null,"温度变送器","P5304出口温度","油脂","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[98,null,"温度变送器","C16出料与原料换热后温度","油脂","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[99,null,"温度变送器","C18出料与原料换热后温度","油脂","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[100,null,"温度变送器","P8603出口温度","油脂","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[101,null,"温度变送器","E5101出料温度","油脂","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[102,null,"温度变送器","E5102出料温度","油脂","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[103,null,"温度变送器","E5101进料温度","油脂","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[104,null,"温度变送器","E5102进料温度","油脂","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[105,null,"温度变送器","V5102尾冷温度","油脂","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[106,null,"温度变送器","脱臭塔中部温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[107,"TICA5205","温度变送器","脱臭塔2层托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[108,"TICA5207","温度变送器","脱臭塔4层托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[109,null,"温度变送器","V5201接收罐温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[110,null,"温度变送器","V5202尾冷接收罐温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[111,null,"温度变送器","V5203蒸汽包温度","蒸汽","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[112,null,"温度变送器","16塔2层填料温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[113,null,"温度变送器","16塔3层填料温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[114,null,"温度变送器","16塔4层填料温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[115,"TICA5306","温度变送器","16塔2层托盘料温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[116,"TICA5308","温度变送器","16塔4层托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[117,null,"温度变送器","V5301接收罐温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[118,null,"温度变送器","V5302尾冷接收罐温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[119,null,"温度变送器","V5305接收罐温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[120,null,"温度变送器","18塔2层填料温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[121,null,"温度变送器","18塔3层填料温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[122,null,"温度变送器","18塔1层托盘料温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[123,"TICA5406","温度变送器","18塔2层托盘料温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[124,null,"温度变送器","18塔3层托盘料温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[125,"TICA5408","温度变送器","18塔4层托盘料温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[126,null,"温度变送器","V5402接收罐温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[127,null,"温度变送器","V5401接收罐温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[128,null,"温度变送器","V5403尾冷接收罐温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[129,null,"温度变送器","V5405蒸汽包温度","蒸汽","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[130,null,"温度变送器","P5409机组循环液罐v5406温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[131,null,"温度变送器","复蒸塔2层填料温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[132,null,"温度变送器","复蒸塔3层填料温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[133,null,"温度变送器","复蒸塔1层填托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[134,"TICA8506","温度变送器","复蒸塔2层填托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[135,null,"温度变送器","复蒸塔3层填托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[136,"TICA8508","温度变送器","复蒸塔4层填托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[137,null,"温度变送器","V8502接收罐温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[138,null,"温度变送器","V8501接收罐温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[139,null,"温度变送器","V8503尾冷接收罐温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[140,null,"温度变送器","V8505蒸汽包温度","蒸汽","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[141,null,"温度变送器","P8506真空机组循环液罐V8506温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[142,"TICA8602","温度变送器","沥青塔2层托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[143,null,"温度变送器","沥青塔3层托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[144,null,"温度变送器","V8601接收罐温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[145,null,"温度变送器","黑脚出料换热后温度","油脂","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[146,null,"温度变送器","导热油总管进油温度","油脂","<0.3","0-300",200,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[147,null,"温度变送器","导热油总管回油温度","油脂","<0.3","0-300",200,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[148,"TIA5203","温度变送器","脱臭塔3层填料温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[149,"TIA5204","温度变送器","脱臭塔1层托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[150,"TIA5206","温度变送器","脱臭塔3层托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[151,"TIA5305","温度变送器","16塔1层托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[152,"TIA5307","温度变送器","16塔3层托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[153,"TIA5314","温度变送器","16塔塔釜循环温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[154,"TIA5404","温度变送器","18塔1层托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[155,null,"温度变送器","18塔塔釜循环温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[156,"TIA8514","温度变送器","复蒸塔塔釜循环温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[157,null,"温度变送器","沥青塔4层托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[158,"TIA8606","温度变送器","沥青塔1层托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[159,"TIA8607","温度变送器","沥青塔塔釜循环温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[160,"TICSA5201","温度变送器","脱臭塔塔顶温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[161,"TICSA5301","温度变送器","16塔塔顶温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[162,"TICSA5401","温度变送器","18塔塔顶温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[163,"TICSA8501","温度变送器","复蒸塔塔顶温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[164,"TICSA8601","温度变送器","沥青塔塔顶温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[165,null,"温度变送器","沥青塔2层托盘温度","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[166,null,"温度变送器","包装车间进料总管温度","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[167,null,"温度变送器","包装车间出料总管温度","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[168,null,"温度变送器","1#搅拌釜温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[169,null,"温度变送器","2#搅拌釜温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[170,null,"温度变送器","3#暂存釜温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[171,null,"温度变送器","4#暂存釜温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[172,null,"温度变送器","卸油池东温度","油脂，酸","<0.3","0-200",2000,"⌀16","DN25","HG20592-09，PN16","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[173,null,"温度变送器","TK125甲醇罐温度","甲醇","<0.3","0-200",4000,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[174,null,"温度变送器","TK126甲醇罐温度","甲醇","<0.3","0-200",4000,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[175,"TISATK101A","温度变送器","TK101甘油罐温度","盐酸，油脂，甘油","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[176,"TISATK102A","温度变送器","TK102废酸罐温度","废酸","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[177,"TISATK103B","温度变送器","TK103废水罐温度","水","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[178,"TISATK104A","温度变送器","TK104（1055）罐温度","盐酸，油脂，甘油","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[179,"TISATK105A","温度变送器","TK105（1055）罐温度","盐酸，油脂，甘油","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[180,"TISATK106A","温度变送器","TK106（1507E）罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[181,"TISATK107A","温度变送器","TK107（1067）罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[182,"TISATK108A","温度变送器","TK108（1065）罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[183,"TISATK109A","温度变送器","TK109（1060）罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[184,"TISATK110A","温度变送器","TK110罐（白土油）温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[185,"TISATK111A","温度变送器","TK111罐（1038）温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[186,"TISATK112A","温度变送器","TK112罐（1030）温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[187,"TISATK113A","温度变送器","TK113罐（甲酯）温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[188,"TISATK114A","温度变送器","TK114罐（甲酯）温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[189,"TISATK115B","温度变送器","TK115罐（中水）温度","水","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[190,"TISATK116A","温度变送器","TK116罐（白土油）温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[191,"TISATK117A","温度变送器","TK117（酸化油）罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[192,"TISATK118A","温度变送器","TK118（原料）罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[193,"TISATK119A","温度变送器","TK119（甲酯）罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[194,"TISATK120A","温度变送器","TK120（原料）罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[195,"TISATK121A","温度变送器","TK121（原料）罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[196,"TISATK122A","温度变送器","TK122（1507）罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[197,"TISATK123A","温度变送器","TK123（甲酯）罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[198,"TISATK124A","温度变送器","TK124（甲酯）罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[199,null,"温度变送器","/","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[200,null,"温度变送器","/","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[201,null,"温度变送器","/","油脂","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[202,null,"温度变送器","/","油脂","<0.3","0-300",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[203,null,"温度变送器","/","油脂","<0.3","0-300",150,"⌀16","M27*2","/","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[204,null,"温度变送器","/","甲醇，油脂，酸","<0.3","0-200",150,"⌀16","M27*2","/","钛","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[205,null,"温度变送器","/","甲醇，油脂，酸","<0.3","0-200",150,"⌀16","DN25","HG20592-09，PN16","钛","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[206,null,"温度变送器","/","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16","316L","Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[207,null,"温度变送器","/","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[208,null,"温度变送器","/","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[209,null,"温度变送器","/","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[210,null,"温度变送器","/","油脂","<0.3","0-300",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[211,null,"温度变送器","/","空气","<0.3","0-200",3300,"⌀6","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[212,null,"温度变送器","/","空气","<0.3","0-200",3600,"⌀6","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[213,"TISA1001","温度变送器","E1107原料预热器出口温度","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[214,"TISA1002","温度变送器","E1108原料预热器出口温度","油脂","<0.3","0-200",150,"⌀16","M27*2","/",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[215,null,"温度变送器","P5307真空机组循环液罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[216,null,"温度变送器","P5406真空机组循环液罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[217,null,"温度变送器","P8509真空机组循环液罐温度","油脂","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"EXdⅡBT4/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[218,"TIA201","温度变送器","M201搅拌温度","油水泥混合物","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"非防爆/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[219,"TIA202","温度变送器","M202搅拌温度","油水泥混合物","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"非防爆/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[220,"TIA203","温度变送器","M203搅拌温度","油水泥混合物","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"非防爆/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]
[221,"TICA204","温度变送器","M206中间进料槽温度","油水泥混合物","<0.3","0-200",400,"⌀16","DN25","HG20592-09，PN16",304,"Pt100",0.2,"非防爆/IP65","M20*1.5","DC24V","2线制","4-20mA和HART","背光LCD",1,null,"上海威尔泰"]

{"sheet":"单法兰液位变送器","index":2,"n_rows":26,"n_cols":32,"rows_kept":26,"merged":[[25,27,25,28]]}
["序号","类别","序号","部门/工段","位号","新位号","仪表名称","测点","介质","设计温度/℃","操作压力/MPa","密度/kg/m3","安装形式","量程/mm","精度要求/%","接液材质","过程连接形式及尺寸","法兰标准及压力等级","信号输出","防爆/防护等级","现场显示","电气接口","接线制","供电电压","单根毛细管长度/mm","天线形式","是否包含排污阀及堵头","接线位置","是否夹套伴热（G1/2\"）","数量/个/台","生产厂家","备注"]
[1,"B",3,"11a","LICA3105",null,"单法兰液位变送器","V3108缓冲罐液位","油脂",65,"常压",860,"侧装","0-70Kpa",0.2,"316L","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[2,"B",4,"11a","LICA3106",null,"单法兰液位变送器","V3113中间缓冲罐液位","油脂",45,"常压",860,"侧装","0-70Kpa",0.2,"316L","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[3,"B",5,"11a","LISA3107",null,"单法兰液位变送器","V3112含醇甘油罐液位","油脂",45,"常压",920,"侧装","0-70Kpa",0.2,"316L","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[4,"B",7,"11a","LIA4106",null,"单法兰液位变送器","V4107沉降罐（1020）液位","油脂",40,"常压",850,"侧装","0-70Kpa",0.2,"316L","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[5,"B",8,"11a","LIA4107",null,"单法兰液位变送器","V4108沉降罐（1020）液位","油脂",40,"常压",850,"侧装","0-70Kpa",0.2,"316L","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[6,"B",20,"11a","LICA1106",null,"单法兰液位变送器","V1108废水中转罐液位","废水","常温","常压",1000,"侧装","0-40Kpa",0.2,"316L","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[7,"B",21,"11a","LIA2101",null,"单法兰液位变送器","V2101酯化原料罐","油脂",105,"常压",860,"侧装","0-40Kpa",0.2,"316L","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[8,"B",30,"11a","LIA2110",null,"单法兰液位变送器","分酸罐V-2106液位","含酸油脂",80,"常压",870,"侧装","0-55KPa",0.2,"衬氟或哈式","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[9,"B",31,"11a","LIA2111",null,"单法兰液位变送器","分酸罐V-2107液位","含酸油脂",80,"常压",870,"侧装","0-55KPa",0.2,"衬氟或哈式","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[10,"B",32,"11a","LISA2112",null,"单法兰液位变送器","V2108FS中转罐液位","废酸",50,"常压",1200,"侧装","0-55KPa",0.2,"衬氟或哈式","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[11,"B",40,"11a","LIA3101",null,"单法兰液位变送器","V3101酯交换原料罐液位","油脂，弱酸",70,"常压",860,"侧装","0-40Kpa",0.2,"衬氟或哈式","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[12,"B",55,"11a","LICA7104",null,"单法兰液位变送器","1020储罐V-7103液位","甘油",35,"常压",1000,"侧装","0-80Kpa",0.2,304,"DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[13,"B",57,"11a","LIA7106",null,"单法兰液位变送器","1020产品分离罐V-7105液位","硫酸，油脂，甘油",50,"常压",1000,"侧装","0-100Kpa",0.2,"衬氟或哈式","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[14,"B",93,41,"LITK103A","LIATK103A","单法兰液位变送器","TK103废水罐液位","水",50,"常压",1000,"侧装","0-150Kpa",0.1,304,"DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[15,"B",105,41,"LIATK115A",null,"单法兰液位变送器","TK115罐（中水）液位","水",50,"常压",1000,"侧装","0-150Kpa",0.1,304,"DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[16,"B",115,41,"LIATK127",null,"单法兰液位变送器","TK127盐酸罐液位","盐酸",35,"常压",1400,"侧装","0-70Kpa",0.1,"衬氟或哈式","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[17,"B",130,"备件","BYLI8001",null,"单法兰液位变送器","/","油脂",105,"常压",860,"侧装","0-60Kpa",0.1,"316L","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[]
[null,null,1,12,"LIA201",null,"单法兰液位变送器","沉淀罐TK201液位","油水泥",100,"常压",900,"侧装","0-100Kpa",0.1,"316L","DN80","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[null,null,2,12,"LIA202",null,"单法兰液位变送器","沉淀罐TK202液位","油水泥",100,"常压",900,"侧装","0-100Kpa",0.1,"316L","DN80","HG20592-09，PN16","4-20mA+HART","非防爆/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[null,null,3,12,"LIA203",null,"单法兰液位变送器","沉淀罐TK203液位","油水泥",100,"常压",900,"侧装","0-100Kpa",0.1,"316L","DN80","HG20592-09，PN16","4-20mA+HART","非防爆/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[null,null,4,12,"LIA204",null,"单法兰液位变送器","循环水罐TK204液位","水",50,"常压",1000,"侧装","0-100Kpa",0.1,"316L","DN80","HG20592-09，PN16","4-20mA+HART","非防爆/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[null,null,5,12,"LIA205",null,"单法兰液位变送器","循环水罐TK205液位","水",50,"常压",1000,"侧装","0-100Kpa",0.1,"316L","DN80","HG20592-09，PN16","4-20mA+HART","非防爆/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[null,null,6,12,"LIA206",null,"单法兰液位变送器","废水罐V204液位","水",50,"常压",1000,"侧装","0-100Kpa",0.1,"316L","DN80","HG20592-09，PN16","4-20mA+HART","非防爆/IP65","LCD","M20*1.5","2线制","DC24V","/","/","/","/","/",1]
[{"$nulls":27},"合计",null,{"$f":"SUM(AD2:AD25)","v":23}]

{"sheet":"双法兰差压变送器","index":3,"n_rows":12,"n_cols":32,"rows_kept":12,"merged":[[11,27,11,28]]}
["序号","类别","序号","部门/工段","位号","新位号","仪表名称","测点","介质","设计温度/℃","操作压力/MPa","密度/kg/m3","安装形式","量程/mm","精度要求/%","接液材质","过程连接形式及尺寸","法兰标准及压力等级","信号输出","防爆/防护等级","现场显示","电气接口","接线制","供电电压","单根毛细管长度/mm","天线形式","是否包含排污阀及堵头","接线位置","是否夹套伴热（G1/2\"）","数量/个/台","生产厂家","备注"]
[1,"A",24,"11a","LICA2104",null,"双法兰差压变送器","反应釜R-2101液位","含酸含醇油脂",110,0.2,860,"侧装","0-60Kpa",0.2,"钽","DN50","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","L:2000\nh:8000","/","/","/","/",1]
[2,"A",25,"11a","LICA2105",null,"双法兰差压变送器","反应釜R-2102液位","含酸含醇油脂",115,0.2,860,"侧装","0-50Kpa",0.2,"钽","DN50","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","L:2000\nh:8000","/","/","/","/",1]
[3,"A",26,"11a","LICA2106",null,"双法兰差压变送器","反应釜R-2103液位","含酸含醇油脂",120,0.2,860,"侧装","0-50Kpa",0.2,"钽","DN50","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","L:2000\nh:8000","/","/","/","/",1]
[4,"A",27,"11a","LICA2107",null,"双法兰差压变送器","反应釜R-2104液位","含酸含醇油脂",80,-0.05,860,"侧装","0-40Kpa",0.2,"钽","DN50","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","L:2000\nh:8000","/","/","/","/",1]
[5,"A",34,"11a","LICA2202",null,"双法兰差压变送器","反应釜R-2201液位","含酸含醇油脂",110,0.2,860,"侧装","0-60Kpa",0.2,"钽","DN50","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","L:2000\nh:8000","/","/","/","/",1]
[6,"A",35,"11a","LICA2203",null,"双法兰差压变送器","反应釜R-2202液位","含酸含醇油脂",115,0.2,860,"侧装","0-50Kpa",0.2,"钽","DN50","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","L:2000\nh:8000","/","/","/","/",1]
[7,"A",36,"11a","LICA2204",null,"双法兰差压变送器","反应釜R-2203液位","含酸含醇油脂",120,0.2,860,"侧装","0-50Kpa",0.2,"钽","DN50","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","L:2000\nh:8000","/","/","/","/",1]
[8,"A",37,"11a","LICA2205",null,"双法兰差压变送器","反应釜R-2204液位","含酸含醇油脂",80,-0.05,860,"侧装","0-40Kpa",0.2,"钽","DN50","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","L:2000\nh:8000","/","/","/","/",1]
[9,"A",56,"11a","LICA7105",null,"双法兰差压变送器","1020处理釜R7101液位","硫酸，油脂，甘油",60,-0.05,1000,"侧装","0-65Kpa",0.2,"钽","DN50","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","L:2000\nh:8000","/","/","/","/",1]
[10,"A",131,"备件","BYLI5001",null,"双法兰差压变送器","/","含酸含醇油脂",110,0.2,860,"侧装","0-60Kpa",0.1,"钽","DN50","HG20592-09，PN16","4-20mA+HART","EXdⅡBT4/IP65","LCD","M20*1.5","2线制","DC24V","L:2000\nh:8000","/","/","/","/",1]
[{"$nulls":27},"合计",null,{"$f":"SUM(AD2:AD11)","v":10}]